ANDHRA PRADESH TRANSMISSION CORPORATION

(AP TRANSCO)

Transformer Fleet Health Assessment Report

Dissolved Gas Analysis (DGA) Based Condition Assessment

Using Machine Learning & IEEE/IEC Standards

Report Date: 28 March 2026

Data Period: 2020-01-02 to 2026-03-20

CONFIDENTIAL

# 1. Executive Summary

This report presents the results of a comprehensive machine learning-based condition assessment of AP Transco’s power transformer fleet. The analysis covers 1,260 transformers across 357 substations, based on 11,932 oil test samples.

## Key Findings

1,104 transformers (88%) in Excellent health (CHI 80–100)

34 transformers require attention (Poor or Critical health)

Average fleet Composite Health Index: 90.8 / 100

Fault classification model: 99.6% accuracy across 8 fault types

30 substations contain at least one Poor transformer

Primary risk factor: Elevated moisture content in transformer oil

## Fleet Risk Distribution

| Risk Level | Count | Percentage | Action Required |
| --- | --- | --- | --- |
| Excellent | 1104 | 87.6% | No action |
| Good | 77 | 6.1% | Continue monitoring |
| Fair | 43 | 3.4% | Increase test frequency |
| Poor | 34 | 2.7% | Plan maintenance |
| Critical | 0 | 0.0% | Immediate action |

# 2. Fault Type Distribution

Each transformer’s latest DGA sample is classified into one of 8 fault types per IEC 60599:2022.

| Fault Code | Description | Count | Key Gases |
| --- | --- | --- | --- |
| Normal | No Fault Detected | 961 | Below IEEE Status 1 |
| T1 | Thermal < 300°C | 165 | CH4, C2H6 |
| T3 | Thermal > 700°C | 44 | C2H4, CH4 |
| D2 | High-energy Discharge | 35 | H2, C2H2, C2H4 |
| D1 | Low-energy Discharge | 29 | H2, C2H2 |
| PD | Partial Discharge | 17 | H2, CH4 |
| T2 | Thermal 300–700°C | 5 | CH4, C2H4, C2H6 |
| DT | Discharge + Thermal | 4 | C2H2, C2H4, CH4 |

# 3. Transformers Requiring Attention

The following 34 transformers are rated Poor or Critical. The ‘Reason for Risk Rating’ column explains which parameter exceeds IEEE/IEC thresholds.

| Equipment | Substation | Make | kV | CHI | Risk | Reason for Risk Rating |
| --- | --- | --- | --- | --- | --- | --- |
| 10016250 | HINDUPUR-220/132/33KV-SUBSTATION | WHEPL | 132 | 25.0 | Poor | Moisture = 63.4 ppm (limit: 30 ppm per IEC 60422) |
| 10069471 | HINDUPUR-220/132/33KV-SUBSTATION | WHE PVT LTD | 132 | 25.0 | Poor | Moisture = 62.2 ppm (limit: 30 ppm per IEC 60422) |
| 10026174 | BANAGANAPALLI-132/33KV-SUBSTATION | CTR | 132 | 25.0 | Poor | Moisture = 42.4 ppm (limit: 30 ppm per IEC 60422) |
| 10047757 | GUDUR-132/33KV-SUBSTATION | HyderabadInstrumentTransformer | 132 | 25.0 | Poor | Moisture = 31.7 ppm (limit: 30 ppm per IEC 60422) |
| 10089409 | KALAPAKA[VIZAG]-400/220KV-SUBSTATIO | EASUN | 400 | 25.0 | Poor | Moisture = 30.5 ppm (limit: 30 ppm per IEC 60422) |
| 10026131 | BANAGANAPALLI-132/33KV-SUBSTATION | PETE | 132 | 25.0 | Poor | Moisture = 33.6 ppm (limit: 30 ppm per IEC 60422) |
| 10040288 | MACHILIPATNAM -132/33KV-SUBSTATION | HIT | 132 | 25.0 | Poor | Moisture = 58.6 ppm (limit: 30 ppm per IEC 60422) |
| 10071077 | AIIMS-132/33/11KV-SUBSTATION | VIJAY | 132 | 25.0 | Poor | Moisture = 36.6 ppm (limit: 30 ppm per IEC 60422) |
| 10070903 | PRATHIPADU-220/132KV-SUBSTATION | BBL | 220 | 25.0 | Poor | Moisture = 54.47 ppm (limit: 30 ppm per IEC 60422) |
| 10070322 | GOOTY[RS]-220/132/33KV-SUBSTATION | CGL | 220 | 25.0 | Poor | Moisture = 43.6 ppm (limit: 30 ppm per IEC 60422) |
| 10107298 | TALARICHERUVU-400/220KV-SUBSTATION | T&R | 400 | 25.0 | Poor | Moisture = 37.8 ppm (limit: 30 ppm per IEC 60422) |
| 10019904 | PORUMAMILLA-132/33KV-SUBSTATION | PETE | 132 | 25.0 | Poor | Moisture = 38.2 ppm (limit: 30 ppm per IEC 60422) |
| 10017028 | TENALI-132/33KV-SUBSTATION | - | 132 | 25.0 | Poor | Moisture = 85.1 ppm (limit: 30 ppm per IEC 60422) |
| 10000013 | ANANDAPURAM-132/33KV-SUBSTATION | WHEP | 132 | 25.0 | Poor | Moisture = 51.9 ppm (limit: 30 ppm per IEC 60422) |
| 10037243 | GANGAVARAM-220/132/33KV-SUBSTATION | HIT | 132 | 25.0 | Poor | Moisture = 48.0 ppm (limit: 30 ppm per IEC 60422) |
| 10110779 | KALAPAKA[VIZAG]-400/220KV-SUBSTATIO | BHEL | 400 | 25.0 | Poor | Moisture = 32.1 ppm (limit: 30 ppm per IEC 60422) |
| 10009615 | PAYAKARAOPETA-132/33KV-SUBSTATION | HPE | 132 | 25.0 | Poor | Moisture = 177.2 ppm (limit: 30 ppm per IEC 60422) |
| 10037402 | GUDIVADA-220/132/33KV-SUBSTATION | PETE | 132 | 25.0 | Poor | Moisture = 50.6 ppm (limit: 30 ppm per IEC 60422) |
| 10012542 | VIZAG SPECIAL ECONOMIC ZONE-132/33K | PETE TRANSFORMER PVT LTD | 132 | 25.0 | Poor | Moisture = 31.5 ppm (limit: 30 ppm per IEC 60422) |
| 10034944 | BAPATLA-132/33KV-SUBSTATION | KEL | 132 | 25.0 | Poor | Moisture = 37.1 ppm (limit: 30 ppm per IEC 60422) |
| 10000446 | AVANIGADDA-132/33KV-SUBSTATION | HIT | 132 | 25.0 | Poor | Moisture = 36.5 ppm (limit: 30 ppm per IEC 60422) |
| 10035593 | CHILAKALURIPET-132/33KV-SUBSTATION | NEI | 132 | 25.0 | Poor | Moisture = 42.2 ppm (limit: 30 ppm per IEC 60422) |
| 10068700 | MUDIGEDU-132/33KV-SUBSTATION | Andrewyule | 132 | 25.0 | Poor | Moisture = 75.9 ppm (limit: 30 ppm per IEC 60422) |
| 10079832 | SALUR-132/33KV-SUBSTATION | HIT | 132 | 25.0 | Poor | Moisture = 34.5 ppm (limit: 30 ppm per IEC 60422) |
| 10115591 | BOBBILI-132/33KV-SUBSTATION | HIT | 132 | 25.0 | Poor | Moisture = 39.7 ppm (limit: 30 ppm per IEC 60422) |
| 10033843 | REPALLE-132/33KV-SUBSTATION | IML | 132 | 25.0 | Poor | Moisture = 39.0 ppm (limit: 30 ppm per IEC 60422) |
| 10033125 | KARAMPUDI-132/33KV-SUBSTATION | BHEL | 132 | 25.0 | Poor | Moisture = 36.0 ppm (limit: 30 ppm per IEC 60422) |
| 10079379 | BRANDIX(ACHUTAPURAM)-220/132/33KV-S | - | 220 | 25.0 | Poor | Moisture = 32.9 ppm (limit: 30 ppm per IEC 60422) |
| 10032550 | TIRUPATI-132/33KV-SUBSTATION | TELK | 132 | 25.0 | Poor | Moisture = 33.4 ppm (limit: 30 ppm per IEC 60422) |
| 10041788 | NARSIPATNAM-132/33KV-SUBSTATION | HINTH T/F PRIVATE LIMITED | 132 | 25.0 | Poor | Moisture = 30.8 ppm (limit: 30 ppm per IEC 60422) |
| 10069198 | PRATHIPADU-132/33KV-SUBSTATION | EMCO | 132 | 25.0 | Poor | Moisture = 41.7 ppm (limit: 30 ppm per IEC 60422) |
| 10026171 | BANAGANAPALLI-132/33KV-SUBSTATION | INDOTECH TRANSFORMERS LIMITED | 132 | 25.0 | Poor | Moisture = 35.3 ppm (limit: 30 ppm per IEC 60422) |
| 10020074 | RAYACHOTY-132/33KV-SS | AMOD | 132 | 35.0 | Poor | Moisture = 148.0 ppm (limit: 30 ppm per IEC 60422); Tan Delta = 0.79 (limit: 1.0 per IEC 60422) |
| 10069285 | PATHAPATNAM-132/33KV-SUBSTATION | NGEF | 132 | 35.0 | Poor | Moisture = 36.3 ppm (limit: 30 ppm per IEC 60422); Acidity = 0.2 mgKOH/g (limit: 0.2 per IEC 60422) |

# 4. Substations with Poor Transformers

30 substations contain at least one transformer rated Poor.

| Substation | kV | Units | Avg CHI | Worst | Last Tested |
| --- | --- | --- | --- | --- | --- |
| ANANDAPURAM-132/33KV-SUBSTATION | 132 | 6 | 80.3 | Poor | 2026-03-05 |
| AIIMS-132/33/11KV-SUBSTATION | 132 | 3 | 58.3 | Poor | 2025-09-18 |
| AVANIGADDA-132/33KV-SUBSTATION | 132 | 3 | 75.0 | Poor | 2025-12-29 |
| BOBBILI-132/33KV-SUBSTATION | 132 | 3 | 68.3 | Poor | 2025-10-15 |
| BANAGANAPALLI-132/33KV-SUBSTATION | 132 | 5 | 51.0 | Poor | 2026-02-25 |
| BAPATLA-132/33KV-SUBSTATION | 132 | 4 | 73.7 | Poor | 2026-02-11 |
| CHILAKALURIPET-132/33KV-SUBSTATION | 132 | 4 | 78.8 | Poor | 2026-02-26 |
| GUDUR-132/33KV-SUBSTATION | 132 | 6 | 82.3 | Poor | 2026-03-15 |
| KARAMPUDI-132/33KV-SUBSTATION | 132 | 3 | 68.1 | Poor | 2026-02-01 |
| MACHILIPATNAM -132/33KV-SUBSTATION | 132 | 4 | 80.2 | Poor | 2026-02-12 |
| MUDIGEDU-132/33KV-SUBSTATION | 132 | 3 | 67.0 | Poor | 2025-11-09 |
| NARSIPATNAM-132/33KV-SUBSTATION | 132 | 4 | 67.3 | Poor | 2026-02-22 |
| PAYAKARAOPETA-132/33KV-SUBSTATION | 132 | 4 | 77.5 | Poor | 2025-12-06 |
| PORUMAMILLA-132/33KV-SUBSTATION | 132 | 3 | 63.5 | Poor | 2025-09-08 |
| PRATHIPADU-132/33KV-SUBSTATION | 132 | 3 | 68.3 | Poor | 2026-02-07 |
| PATHAPATNAM-132/33KV-SUBSTATION | 132 | 2 | 58.1 | Poor | 2025-07-30 |
| RAYACHOTY-132/33KV-SS | 132 | 3 | 78.3 | Poor | 2025-12-18 |
| REPALLE-132/33KV-SUBSTATION | 132 | 3 | 73.1 | Poor | 2025-12-23 |
| SALUR-132/33KV-SUBSTATION | 132 | 4 | 69.6 | Poor | 2025-11-28 |
| TENALI-132/33KV-SUBSTATION | 132 | 5 | 82.0 | Poor | 2026-01-21 |
| TIRUPATI-132/33KV-SUBSTATION | 132 | 2 | 37.5 | Poor | 2026-01-22 |
| VIZAG SPECIAL ECONOMIC ZONE-132/33KV-SS | 132 | 3 | 71.2 | Poor | 2025-11-14 |
| BRANDIX(ACHUTAPURAM)-220/132/33KV-SS | 132 | 7 | 79.2 | Poor | 2026-02-19 |
| GUDIVADA-220/132/33KV-SUBSTATION | 132 | 8 | 85.1 | Poor | 2025-12-08 |
| GOOTY[RS]-220/132/33KV-SUBSTATION | 132 | 5 | 83.2 | Poor | 2025-09-10 |
| GANGAVARAM-220/132/33KV-SUBSTATION | 132 | 7 | 85.2 | Poor | 2025-10-21 |
| HINDUPUR-220/132/33KV-SUBSTATION | 132 | 10 | 79.4 | Poor | 2025-12-29 |
| PRATHIPADU-220/132KV-SUBSTATION | 220 | 6 | 78.3 | Poor | 2026-03-20 |
| KALAPAKA[VIZAG]-400/220KV-SUBSTATION | 400 | 21 | 82.0 | Poor | 2026-02-06 |
| TALARICHERUVU-400/220KV-SUBSTATION | 400 | 7 | 74.3 | Poor | 2025-08-25 |

# 5. Manufacturer Performance

| Manufacturer | Units | Avg CHI | Fault Rate | Poor/Crit | Assessment |
| --- | --- | --- | --- | --- | --- |
| BBL | 96 | 96.0 | 12.5% | 1 | Needs review |
| TOSHIBA | 95 | 95.9 | 36.8% | 0 | OK |
| T&R | 84 | 92.3 | 23.8% | 1 | Needs review |
| BHEL | 76 | 91.0 | 18.4% | 2 | Needs review |
| EMCO | 66 | 86.7 | 19.7% | 1 | Needs review |
| NGEF | 64 | 85.9 | 26.6% | 1 | Needs review |
| ECE | 63 | 96.6 | 12.7% | 0 | OK |
| APEX | 52 | 86.3 | 40.4% | 0 | High fault rate |
| TELK | 49 | 92.5 | 22.4% | 1 | Needs review |
| BHARAT BIJILI LIMITED | 45 | 92.2 | 15.6% | 0 | OK |
| ECE INDUSTRIES LTD | 41 | 98.7 | 2.4% | 0 | OK |
| CROMPTON GREAVES LTD(CGL) | 27 | 93.1 | 40.7% | 0 | High fault rate |
| CGL | 19 | 87.0 | 21.1% | 1 | Needs review |
| INDOTECH TRANSFORMERS LIMITED | 19 | 89.8 | 15.8% | 1 | Needs review |
| ANDREWYULE & COMPANY LTD. | 17 | 90.9 | 35.3% | 0 | OK |
| ALSTOM | 16 | 94.7 | 18.8% | 0 | OK |
| Unknown | 16 | 85.3 | 12.5% | 2 | Needs review |
| ETE | 13 | 83.8 | 61.5% | 0 | High fault rate |
| TRIL | 13 | 96.6 | 30.8% | 0 | OK |
| TBEA | 12 | 99.7 | 16.7% | 0 | OK |
| AVAL | 12 | 96.8 | 58.3% | 0 | High fault rate |
| VIJAY ELECTRICALS | 12 | 90.9 | 33.3% | 0 | OK |
| TR | 11 | 96.8 | 36.4% | 0 | OK |
| INDOTECH | 10 | 89.5 | 10.0% | 0 | OK |

# 6. Machine Learning Model Performance

## Model 1: Fault Classification

Accuracy: 99.6% | Weighted F1: 99.6% | Macro F1: 97.9%

| Fault | Precision | Recall | F1 | Support |
| --- | --- | --- | --- | --- |
| Normal | 100.0% | 100.0% | 100.0% | 578 |
| PD | 97.4% | 100.0% | 98.7% | 37 |
| D1 | 97.3% | 98.6% | 98.0% | 73 |
| D2 | 98.7% | 97.4% | 98.0% | 77 |
| T1 | 99.6% | 99.6% | 99.6% | 255 |
| T2 | 100.0% | 80.0% | 88.9% | 5 |
| T3 | 100.0% | 100.0% | 100.0% | 115 |
| DT | 100.0% | 100.0% | 100.0% | 23 |

## Model 2: Health Index Regression

R²: 0.9923 | RMSE: 1.36 | MAE: 0.48 | Risk Accuracy: 98.3%

## Model 3: Failure Prediction

Accuracy: 93.4% | AUC-ROC: 0.860 | AUC-PR: 0.486

# 7. Methodology & Standards

## Standards Applied

IEEE C57.104-2019 — Gas concentration thresholds (Status 1/2/3), rate limits, Rogers ratios, Key Gas method

IEC 60599:2022 — Fault taxonomy (PD/D1/D2/T1/T2/T3/DT), Duval Triangle, IEC ratio method

CIGRE TB 771 (2019) — Duval Pentagon 5-gas centroid classification

IEC 60422:2013 — Oil quality thresholds (BDV, moisture, acidity, tan delta)

## Health Index Formula

CHI = 50% × DGAF + 15% × BDV + 15% × Moisture + 10% × Acidity + 10% × Tan Delta

## Data Integrity

All gas values from actual last sample date per transformer (not aggregated)

Fault labels generated by 5-method weighted consensus voting

Temporal train/test split for failure prediction (no data leakage)

Gas data completeness varies: Key Gas 83%, Duval methods 10–15%

Oil BDV data sparse (1.5%) — CHI redistributes weight proportionally

## Research References

[1] ML-based multi-method DGA interpretation — PMC/ScienceDirect, 2024

[2] Fault Classification via DGA and ML: Systematic Review — MDPI Applied Sciences, 2025

[3] Evaluation of Duval Pentagon — Springer Electrical Engineering, 2025

[4] Review of Transformer Health Index — MDPI Electronics, 2023

[5] Modified DGA Scoring with Rate Values — MDPI Energies, 2024

[6] SHAP + LGBM for DGA Fault Diagnosis — Energy Informatics, 2025

[7] SMOTE + GBDT Hybrid for DGA — Arabian J. Sci. Eng., 2025

— End of Report —

Generated: 28 March 2026 | AP Transco DGA Dashboard — Phase A Local Analysis